## Tarutung
Proyek |  |  | : REHABILITASI DAN PENGADAAN SCADA SISTEM SUMUT - ACEH | [15 empty] | No. Dokumen : | INSTP/RTU
Customer |  |  | : PT PLN (PERSERO) PENYALURAN & PUSAT PENGATUR BEBAN SUMATERA | [15 empty] | Revisi : | 1
No Kontrak PLN |  |  | : 002.PJ/612/GM.P3B-Sumatera/2006
Kontraktor |  |  | : PT. SIEMENS INDONESIA
No Kontrak Siemens |  |  | : 340P-30064 | [15 empty] | Tanggal : | 10 April 2007
PERINCIAN KEBUTUHAN I/O POINT RTU
Substation Name |  | : TARUTUNG |  | RTU ID :
TYPE | NO | MNEMO | DESIGNATION / FUNCTION | BAY NAME | [16 empty] | Total Quantity of I/O datas
|  |  |  | COMMON | PORSEA 1 | PORSEA 2 | SIBOLGA 1 | SIBOLGA 2 | SIDIKALANG | TELE | KOPEL | TRF52-1 | TRF52-2 | BUSBAR 1 | BUSBAR 2 | INCOMING TD1 | INCOMING TD2
IED | 1 | HZ | FREQUENCY | [10 empty] | 1 | 1 | 1 | 1
| 2 | KV | VOLTS |  | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1
| 3 | A | AMPERES
| 4 | MW | MEGAWATTS
| 5 | MX | MEGAVARS
TOTAL |  |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 12
TSS | 1 | LRCB | LOCAL/REMOTE SWITCH FOR CB |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1
| 2 | LRTC | LOCAL/REMOTE SWITCH FOR TC | [8 empty] | 1 | 1
| 3 | BF | BAY FAULT |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 4 | BRF | BREAKER FAULT |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 5 | P1 | PROTECTION CLASS 1 TRIP |  | 1 | 1 | 1 | 1 | 1 | 1
| 6 | AR | CB AUTO RECLOSER |  | 1 | 1 | 1 | 1 | 1 | 1
| 7 | P2 | PROTECTION CLASS 2 TRIP |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
| 8 | P3 | PROTECTION CLASS 3 TRIP | [10 empty] | 1 | 1
| 9 | VS | VOLTAGE STATUS | [10 empty] | 1 | 1
| 10 | TRA | TRANSFORMER ALARM | [8 empty] | 1 | 1
| 11 | TCT | TAP CHANGER TRIP | [8 empty] | 1 | 1
| 12 | TCA | TAP CHANGER ALARM | [8 empty] | 1 | 1
| 13 | TCH | TAP CHANGER HIGH LIMIT | [8 empty] | 1 | 1
| 14 | TCL | TAP CHANGER LOW LIMIT | [8 empty] | 1 | 1
| 15 | CD | CONTROL DISABLE SWITCH | 1
| 16 | RTU | RTU ALARM | 1
| 17 | COM | COMMUNICATION ALARM | 1
| 18 | SUF | SUBSTATION URGENT FAULT (MPS) | 1
| 19 | SNF | SUBSTATION NON URGENT FAULT (SPS) | 1
| 20 | TTT | TELEPROTECTION TRIP TRANSMITTED |  | 1 | 1 | 1 | 1 | 1 | 1
| 21 | TTR | TELEPROTECTION TRIP RECEIVED |  | 1 | 1 | 1 | 1 | 1 | 1
| 22 | CSP | CHECK SYNCHRONIZING IN PROGRESS |  | 1 | 1 | 1 | 1 | 1 | 1 | 1
TSS | 23 | LT | LINE TRIP
| 24 | LRB I | LOCAL/REMOTE SWITCH FOR BI1) |  | 2 |  | 2 |  |  |  |  | 2
| 25 | TRT | TRANSFORMER TRIP1) | [8 empty] | 1 | 1
| 26 | TEA | TRANSFORMER TEMPERATURE ALARM1) | [8 empty] | 1 | 1
| 27 | TET | TRANSFORMER TEMPERATURE TRIP1) | [8 empty] | 1 | 1
TOTAL |  |  |  | 5 | 11 | 9 | 11 | 9 | 9 | 9 | 5 | 14 | 12 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | 100
TSD | 1 | CB | CIRCUIT BREAKER CLOSED/OPENED |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1
| 2 | BI | BUS ISOLATOR SWITCH CLOSED/OPENED |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| 3 | TCC | TAP CHANGER AUTO/MANUAL | [8 empty] | 1 | 1
| 4 | LI | LINE ISOLATOR SWITCH CLOSED/OPENED |  | 1 | 1 | 1 | 1 | 1 | 1
| 5 | ES | EARTH SWITCH CLOSED/OPENED (MANUAL) |  | 1 | 1 | 1 | 1 | 1 | 1
| 6 | RACK | CIRCUIT BREAKER RACKIN/RACKOUT
| 7 | DCBC | DUMMY BREAKER CLOSED/OPENED | 1
| 8 | GFM | GOVERNOR FREE MODE
| 9 | LLM | LOAD LIMIT LOAD
TOTAL |  |  |  | 1 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 4 | 4 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 44
RCD | 1 | CB | CIRCUIT BREAKER CLOSED/OPENED |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  | 1 | 1
| 2 | BI | BUS ISOLATOR SWITCH CLOSED/OPENED |  | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2
| 3 | TCC | TAP CHANGER AUTO/MANUAL | [8 empty] | 1 | 1
| 4 | DCBC | DUMMY BREAKER CLOSED/OPENED | 1
TOTAL |  |  |  | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 1 | 4 | 4 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 30
Note :
1). The signal is not stated on RKS. |  |  |  | IO Point | [6 empty] | Total IO and IED :
|  |  |  | IED |  |  | 12 |  |  |  | IED |  | 12
|  |  |  | TSS |  |  | 100 |  |  |  | TS |  | 188
|  |  |  | TSD |  |  | 44 |  |  |  | RCD |  | 30
|  |  |  | RCD |  |  | 30

## RC
Proyek |  |  | : REHABILITASI DAN PENGADAAN SCADA SISTEM SUMUT - ACEH | [10 empty] | No. Dokumen : | INSTP/RTU
Customer |  |  | : PT PLN (PERSERO) PENYALURAN & PUSAT PENGATUR BEBAN SUMATERA | [10 empty] | Revisi : | 1
No Kontrak PLN |  |  | : 002.PJ/612/GM.P3B-Sumatera/2006
Kontraktor |  |  | : PT. SIEMENS INDONESIA
No Kontrak Siemens |  |  | : 340P-30064 | [10 empty] | Tanggal : | 10 April 2007
RTU WIRING & AFFECTATION MODULES
Name of Substation |  |  | : TARUTUNG
Number of CPU |  |  | : 2
Name of Module |  |  | : HDO 040 ( 2 cards) for RC
NO | DATABASE |  |  |  | ADDRESS | TYPE DATA | CELL NUMBER | SLOT NUMBER | PORT NUMBER | CONTROL NUMBER | INTERFACE. 37 PIN |  | TERMINAL BLOCK |  |  | REMARKS
| VOLTAGE | BAY NAME | DEVICE | DATA | [6 empty] | INTF No. | Pin No. | GROUP | NO | TAG
1 | 150 | Common | DCBC | Open | 0/4/1 | RC | 1 | 5 | A | RC1 - 1 | RC1 - A | 1 | TB-1 | 3 | DCBCcCB-O | COMMON
2 | 150 | Common | DCBC | Close |  | RC | 1 | 5 | A | RC1 - 2 | RC1 - A | 2 | TB-1 | 4 | DCBCcCB-C | COMMON
3 | 150 | KOPEL | CB | Open | 0/4/2 | RC | 1 | 5 | A | RC1 - 3 | RC1 - A | 3 | TB-2 | 6 | KOPELcCB-O | KOPEL
4 | 150 | KOPEL | CB | Close |  | RC | 1 | 5 | A | RC1 - 4 | RC1 - A | 4 | TB-2 | 7 | KOPELcCB-C | KOPEL
5 | 150 | PRSEA2 | CB | Open | 0/4/3 | RC | 1 | 5 | A | RC1 - 5 | RC1 - A | 5 | TB-3 | 6 | PRSEA2cCB-O | PORSEA 2
6 | 150 | PRSEA2 | CB | Close |  | RC | 1 | 5 | A | RC1 - 6 | RC1 - A | 6 | TB-3 | 7 | PRSEA2cCB-C | PORSEA 2
7 | 150 | PRSEA2 | BI1 | Open | 0/4/4 | RC | 1 | 5 | A | RC1 - 7 | RC1 - A | 7 | TB-3 | 8 | PRSEA2cBI1-O | PORSEA 2
8 | 150 | PRSEA2 | BI1 | Close |  | RC | 1 | 5 | A | RC1 - 8 | RC1 - A | 8 | TB-3 | 9 | PRSEA2cBI1-C | PORSEA 2
9 | 150 | PRSEA2 | BI2 | Open | 0/4/5 | RC | 1 | 5 | A | RC1 - 9 | RC1 - A | 9 | TB-3 | 10 | PRSEA2cBI2-O | PORSEA 2
10 | 150 | PRSEA2 | BI2 | Close |  | RC | 1 | 5 | A | RC1 - 10 | RC1 - A | 10 | TB-3 | 11 | PRSEA2cBI2-C | PORSEA 2
11 | 150 | SBLGA2 | CB | Open | 0/4/6 | RC | 1 | 5 | A | RC1 - 11 | RC1 - A | 11 | TB-4 | 6 | SBLGA2cCB-O | SIBOLGA 2
12 | 150 | SBLGA2 | CB | Close |  | RC | 1 | 5 | A | RC1 - 12 | RC1 - A | 12 | TB-4 | 7 | SBLGA2cCB-C | SIBOLGA 2
13 | 150 | SBLGA2 | BI1 | Open | 0/4/7 | RC | 1 | 5 | A | RC1 - 13 | RC1 - A | 13 | TB-4 | 8 | SBLGA2cBI1-O | SIBOLGA 2
14 | 150 | SBLGA2 | BI1 | Close |  | RC | 1 | 5 | A | RC1 - 14 | RC1 - A | 14 | TB-4 | 9 | SBLGA2cBI1-C | SIBOLGA 2
15 | 150 | SBLGA2 | BI2 | Open | 0/4/8 | RC | 1 | 5 | A | RC1 - 15 | RC1 - A | 15 | TB-4 | 10 | SBLGA2cBI2-O | SIBOLGA 2
16 | 150 | SBLGA2 | BI2 | Close |  | RC | 1 | 5 | A | RC1 - 16 | RC1 - A | 16 | TB-4 | 11 | SBLGA2cBI2-C | SIBOLGA 2
17 | 150 | SDKLG1 | CB | Open | 0/4/9 | RC | 1 | 5 | B | RC1 - 17 | RC1 - B | 1 | TB-5 | 6 | SDKLG1cCB-O | SIDIKALANG 1
18 | 150 | SDKLG1 | CB | Close |  | RC | 1 | 5 | B | RC1 - 18 | RC1 - B | 2 | TB-5 | 7 | SDKLG1cCB-C | SIDIKALANG 1
19 | 150 | SDKLG1 | BI1 | Open | 0/4/10 | RC | 1 | 5 | B | RC1 - 19 | RC1 - B | 3 | TB-5 | 8 | SDKLG1cBI1-O | SIDIKALANG 1
20 | 150 | SDKLG1 | BI1 | Close |  | RC | 1 | 5 | B | RC1 - 20 | RC1 - B | 4 | TB-5 | 9 | SDKLG1cBI1-C | SIDIKALANG 1
21 | 150 | SDKLG1 | BI2 | Open | 0/4/11 | RC | 1 | 5 | B | RC1 - 21 | RC1 - B | 5 | TB-5 | 10 | SDKLG1cBI2-O | SIDIKALANG 1
22 | 150 | SDKLG1 | BI2 | Close |  | RC | 1 | 5 | B | RC1 - 22 | RC1 - B | 6 | TB-5 | 11 | SDKLG1cBI2-C | SIDIKALANG 1
23 | 150 | TELE1 | CB | Open | 0/4/12 | RC | 1 | 5 | B | RC1 - 23 | RC1 - B | 7 | TB-6 | 6 | TELE1cCB-O | TELE 1
24 | 150 | TELE1 | CB | Close |  | RC | 1 | 5 | B | RC1 - 24 | RC1 - B | 8 | TB-6 | 7 | TELE1cCB-C | TELE 1
25 | 150 | TELE1 | BI1 | Open | 0/4/13 | RC | 1 | 5 | B | RC1 - 25 | RC1 - B | 9 | TB-6 | 8 | TELE1cBI1-O | TELE 1
26 | 150 | TELE1 | BI1 | Close |  | RC | 1 | 5 | B | RC1 - 26 | RC1 - B | 10 | TB-6 | 9 | TELE1cBI1-C | TELE 1
27 | 150 | TELE1 | BI2 | Open | 0/4/14 | RC | 1 | 5 | B | RC1 - 27 | RC1 - B | 11 | TB-6 | 10 | TELE1cBI2-O | TELE 1
28 | 150 | TELE1 | BI2 | Close |  | RC | 1 | 5 | B | RC1 - 28 | RC1 - B | 12 | TB-6 | 11 | TELE1cBI2-C | TELE 1
29 | 150 | PRSEA1 | CB | Open | 0/4/15 | RC | 1 | 5 | B | RC1 - 29 | RC1 - B | 13 | TB-7 | 6 | PRSEA1cCB-O | PORSEA 1
30 | 150 | PRSEA1 | CB | Close |  | RC | 1 | 5 | B | RC1 - 30 | RC1 - B | 14 | TB-7 | 7 | PRSEA1cCB-C | PORSEA 1
31 | 150 | PRSEA1 | BI1 | Open | 0/4/16 | RC | 1 | 5 | B | RC1 - 31 | RC1 - B | 15 | TB-7 | 8 | PRSEA1cBI1-O | PORSEA 1
32 | 150 | PRSEA1 | BI1 | Close |  | RC | 1 | 5 | B | RC1 - 32 | RC1 - B | 16 | TB-7 | 9 | PRSEA1cBI1-C | PORSEA 1
33 | 150 | PRSEA1 | BI2 | Open | 0/4/17 | RC | 2 | 7 | A | RC2 - 1 | RC2 - A | 1 | TB-7 | 10 | PRSEA1cBI2-O | PORSEA 1
34 | 150 | PRSEA1 | BI2 | Close |  | RC | 2 | 7 | A | RC2 - 2 | RC2 - A | 2 | TB-7 | 11 | PRSEA1cBI2-C | PORSEA 1
35 | 150 | SBLGA1 | CB | Open | 0/4/18 | RC | 2 | 7 | A | RC2 - 3 | RC2 - A | 3 | TB-8 | 6 | SBLGA1cCB-O | SIBOLGA 1
36 | 150 | SBLGA1 | CB | Close |  | RC | 2 | 7 | A | RC2 - 4 | RC2 - A | 4 | TB-8 | 7 | SBLGA1cCB-C | SIBOLGA 1
37 | 150 | SBLGA1 | BI1 | Open | 0/4/19 | RC | 2 | 7 | A | RC2 - 5 | RC2 - A | 5 | TB-8 | 8 | SBLGA1cBI1-O | SIBOLGA 1
38 | 150 | SBLGA1 | BI1 | Close |  | RC | 2 | 7 | A | RC2 - 6 | RC2 - A | 6 | TB-8 | 9 | SBLGA1cBI1-C | SIBOLGA 1
39 | 150 | SBLGA1 | BI2 | Open | 0/4/20 | RC | 2 | 7 | A | RC2 - 7 | RC2 - A | 7 | TB-8 | 10 | SBLGA1cBI2-O | SIBOLGA 1
40 | 150 | SBLGA1 | BI2 | Close |  | RC | 2 | 7 | A | RC2 - 8 | RC2 - A | 8 | TB-8 | 11 | SBLGA1cBI2-C | SIBOLGA 1
41 | 150 | TRF521 | CB | Open | 0/4/21 | RC | 2 | 7 | A | RC2 - 9 | RC2 - A | 9 | TB-9 | 6 | TRAFO1cCB-O | TRF521
42 | 150 | TRF521 | CB | Close |  | RC | 2 | 7 | A | RC2 - 10 | RC2 - A | 10 | TB-9 | 7 | TRAFO1cCB-C | TRF521
43 | 150 | TRF521 | BI1 | Open | 0/4/22 | RC | 2 | 7 | A | RC2 - 11 | RC2 - A | 11 | TB-9 | 8 | TRAFO1cBI1-O | TRF521
44 | 150 | TRF521 | BI1 | Close |  | RC | 2 | 7 | A | RC2 - 12 | RC2 - A | 12 | TB-9 | 9 | TRAFO1cBI1-C | TRF521
45 | 150 | TRF521 | BI2 | Open | 0/4/23 | RC | 2 | 7 | A | RC2 - 13 | RC2 - A | 13 | TB-9 | 10 | TRAFO1cBI2-O | TRF521
46 | 150 | TRF521 | BI2 | Close |  | RC | 2 | 7 | A | RC2 - 14 | RC2 - A | 14 | TB-9 | 11 | TRAFO1cBI2-C | TRF521
47 | 150 | TRF521 | TCC | Auto | 0/4/24 | RC | 2 | 7 | A | RC2 - 15 | RC2 - A | 15 | TB-9 | 12 | TRAFO1cTCC-A | TRF521
48 | 150 | TRF521 | TCC | Manual |  | RC | 2 | 7 | A | RC2 - 16 | RC2 - A | 16 | TB-9 | 13 | TRAFO1cTCC-M | TRF521
49 | 150 | TRF522 | CB | Open | 0/4/25 | RC | 2 | 7 | B | RC2 - 17 | RC2 - B | 1 | TB-10 | 6 | TRAFO2cCB-O | TRF522
50 | 150 | TRF522 | CB | Close |  | RC | 2 | 7 | B | RC2 - 18 | RC2 - B | 2 | TB-10 | 7 | TRAFO2cCB-C | TRF522
51 | 150 | TRF522 | BI1 | Open | 0/4/26 | RC | 2 | 7 | B | RC2 - 19 | RC2 - B | 3 | TB-10 | 8 | TRAFO2cBI1-O | TRF522
52 | 150 | TRF522 | BI1 | Close |  | RC | 2 | 7 | B | RC2 - 20 | RC2 - B | 4 | TB-10 | 9 | TRAFO2cBI1-C | TRF522
53 | 150 | TRF522 | BI2 | Open | 0/4/27 | RC | 2 | 7 | B | RC2 - 21 | RC2 - B | 5 | TB-10 | 10 | TRAFO2cBI2-O | TRF522
54 | 150 | TRF522 | BI2 | Close |  | RC | 2 | 7 | B | RC2 - 22 | RC2 - B | 6 | TB-10 | 11 | TRAFO2cBI2-C | TRF522
55 | 150 | TRF522 | TCC | Auto | 0/4/28 | RC | 2 | 7 | B | RC2 - 23 | RC2 - B | 7 | TB-10 | 12 | TRAFO2cTCC-A | TRF522
56 | 150 | TRF522 | TCC | Manual |  | RC | 2 | 7 | B | RC2 - 24 | RC2 - B | 8 | TB-10 | 13 | TRAFO2cTCC-M | TRF522
57 | 20 | INCTD-1 | CB | Open | 0/4/29 | RC | 2 | 7 | B | RC2 - 25 | RC2 - B | 9
58 | 20 | INCTD-1 | CB | Close |  | RC | 2 | 7 | B | RC2 - 26 | RC2 - B | 10
59 | 20 | INCTD-2 | CB | Open | 0/4/30 | RC | 2 | 7 | B | RC2 - 27 | RC2 - B | 11
60 | 20 | INCTD-2 | CB | Close |  | RC | 2 | 7 | B | RC2 - 28 | RC2 - B | 12
61 | ……………………………………... Spare ……………...…………………...…….. |  |  |  |  | RC | 2 | 7 | B | RC2 - 29 | RC2 - B | 13
62 | ……………………………………... Spare ……………...…………………...…….. |  |  |  |  | RC | 2 | 7 | B | RC2 - 30 | RC2 - B | 14
63 | ……………………………………... Spare ……………...…………………...…….. |  |  |  |  | RC | 2 | 7 | B | RC2 - 31 | RC2 - B | 15
64 | ……………………………………... Spare ……………...…………………...…….. |  |  |  |  | RC | 2 | 7 | B | RC2 - 32 | RC2 - B | 16
|  |  |  | 1024 | 0/4/0
|  |  |  | 1041 | 0/4/17
|  |  |  | 1048 | 0/4/24
|  |  |  | 1049 | 0/4/25

## DI
Proyek |  |  | : REHABILITASI DAN PENGADAAN SCADA SISTEM SUMUT - ACEH | [10 empty] | No. Dokumen : | INSTP/RTU
Customer |  |  | : PT PLN (PERSERO) PENYALURAN & PUSAT PENGATUR BEBAN SUMATERA | [10 empty] | Revisi : | 1
No Kontrak PLN |  |  | : 002.PJ/612/GM.P3B-Sumatera/2006
Kontraktor |  |  | : PT. SIEMENS INDONESIA
No Kontrak Siemens |  |  | : 340P-30064 | [10 empty] | Tanggal : | 10 April 2007
RTU WIRING & AFFECTATION MODULES
Name of Substation |  |  | : TARUTUNG
Number of CPU |  |  | : 2
Name of Module |  |  | : HDI050 ( 3 cards) for TS
NO | DATABASE |  |  |  | ADDRESS | TYPE DATA | CELL NUMBER | SLOT NUMBER | PORT | INPUT NUMBER | INTERFACE. 37 PIN |  | TERMINAL BLOCK |  |  | REMARKS
| VOLTAGE | BAY NAME | DEVICE | DATA | [6 empty] | INTF No. | Pin No. | GROUP | NO | TAG
1 | 150 | Common | DCBC | Open | 0/16/1 | TSD | 1 | 2 | A | DI1 - 1 | DI1 - A | 1 | TB-1 | 5 | DCBCdCB-O | COMMON
2 | 150 | Common | DCBC | Close |  | TSD | 1 | 2 | A | DI1 - 2 | DI1 - A | 20 | TB-1 | 6 | DCBCdCB-C | COMMON
3 | 150 | KOPEL | CB | Open | 0/16/2 | TSD | 1 | 2 | A | DI1 - 3 | DI1 - A | 2 | TB-2 | 8 | KOPELdCB-O | KOPEL
4 | 150 | KOPEL | CB | Close |  | TSD | 1 | 2 | A | DI1 - 4 | DI1 - A | 21 | TB-2 | 9 | KOPELdCB-C | KOPEL
5 | 150 | KOPEL | BI1 | Open | 0/16/3 | TSD | 1 | 2 | A | DI1 - 5 | DI1 - A | 3 | TB-2 | 10 | KOPELdBI1-O | KOPEL
6 | 150 | KOPEL | BI1 | Close |  | TSD | 1 | 2 | A | DI1 - 6 | DI1 - A | 22 | TB-2 | 11 | KOPELdBI1-C | KOPEL
7 | 150 | KOPEL | BI2 | Open | 0/16/4 | TSD | 1 | 2 | A | DI1 - 7 | DI1 - A | 4 | TB-2 | 12 | KOPELdBI2-O | KOPEL
8 | 150 | KOPEL | BI2 | Close |  | TSD | 1 | 2 | A | DI1 - 8 | DI1 - A | 23 | TB-2 | 13 | KOPELdBI2-C | KOPEL
9 | 150 | PRSEA2 | CB | Open | 0/16/5 | TSD | 1 | 2 | A | DI1 - 9 | DI1 - A | 5 | TB-3 | 12 | PRSEA2dCB-O | PORSEA 2
10 | 150 | PRSEA2 | CB | Close |  | TSD | 1 | 2 | A | DI1 - 10 | DI1 - A | 24 | TB-3 | 13 | PRSEA2dCB-C | PORSEA 2
11 | 150 | PRSEA2 | BI1 | Open | 0/16/6 | TSD | 1 | 2 | A | DI1 - 11 | DI1 - A | 6 | TB-3 | 14 | PRSEA2dBI1-O | PORSEA 2
12 | 150 | PRSEA2 | BI1 | Close |  | TSD | 1 | 2 | A | DI1 - 12 | DI1 - A | 25 | TB-3 | 15 | PRSEA2dBI1-C | PORSEA 2
13 | 150 | PRSEA2 | BI2 | Open | 0/16/7 | TSD | 1 | 2 | A | DI1 - 13 | DI1 - A | 7 | TB-3 | 16 | PRSEA2dBI2-O | PORSEA 2
14 | 150 | PRSEA2 | BI2 | Close |  | TSD | 1 | 2 | A | DI1 - 14 | DI1 - A | 26 | TB-3 | 17 | PRSEA2dBI2-C | PORSEA 2
15 | 150 | PRSEA2 | LI | Open | 0/16/8 | TSD | 1 | 2 | A | DI1 - 15 | DI1 - A | 8 | TB-3 | 18 | PRSEA2dLI-O | PORSEA 2
16 | 150 | PRSEA2 | LI | Close |  | TSD | 1 | 2 | A | DI1 - 16 | DI1 - A | 27 | TB-3 | 19 | PRSEA2dLI-C | PORSEA 2
17 | 150 | PRSEA2 | ES | Open | 0/16/9 | TSD | 1 | 2 | A | DI1 - 17 | DI1 - A | 10 | TB-3 | 20 | PRSEA2dES-O | PORSEA 2
18 | 150 | PRSEA2 | ES | Close |  | TSD | 1 | 2 | A | DI1 - 18 | DI1 - A | 29 | TB-3 | 21 | PRSEA2dES-C | PORSEA 2
19 | 150 | SBLGA2 | CB | Open | 0/16/10 | TSD | 1 | 2 | A | DI1 - 19 | DI1 - A | 11 | TB-4 | 12 | SBLGA2dCB-O | SIBOLGA 2
20 | 150 | SBLGA2 | CB | Close |  | TSD | 1 | 2 | A | DI1 - 20 | DI1 - A | 30 | TB-4 | 13 | SBLGA2dCB-C | SIBOLGA 2
21 | 150 | SBLGA2 | BI1 | Open | 0/16/11 | TSD | 1 | 2 | A | DI1 - 21 | DI1 - A | 12 | TB-4 | 14 | SBLGA2dBI1-O | SIBOLGA 2
22 | 150 | SBLGA2 | BI1 | Close |  | TSD | 1 | 2 | A | DI1 - 22 | DI1 - A | 31 | TB-4 | 15 | SBLGA2dBI1-C | SIBOLGA 2
23 | 150 | SBLGA2 | BI2 | Open | 0/16/12 | TSD | 1 | 2 | A | DI1 - 23 | DI1 - A | 13 | TB-4 | 16 | SBLGA2dBI2-O | SIBOLGA 2
24 | 150 | SBLGA2 | BI2 | Close |  | TSD | 1 | 2 | A | DI1 - 24 | DI1 - A | 32 | TB-4 | 17 | SBLGA2dBI2-C | SIBOLGA 2
25 | 150 | SBLGA2 | LI | Open | 0/16/13 | TSD | 1 | 2 | A | DI1 - 25 | DI1 - A | 14 | TB-4 | 18 | SBLGA2dLI-O | SIBOLGA 2
26 | 150 | SBLGA2 | LI | Close |  | TSD | 1 | 2 | A | DI1 - 26 | DI1 - A | 33 | TB-4 | 19 | SBLGA2dLI-C | SIBOLGA 2
27 | 150 | SBLGA2 | ES | Open | 0/16/14 | TSD | 1 | 2 | A | DI1 - 27 | DI1 - A | 15 | TB-4 | 20 | SBLGA2dES-O | SIBOLGA 2
28 | 150 | SBLGA2 | ES | Close |  | TSD | 1 | 2 | A | DI1 - 28 | DI1 - A | 34 | TB-4 | 21 | SBLGA2dES-C | SIBOLGA 2
29 | 150 | SDKLG1 | CB | Open | 0/16/15 | TSD | 1 | 2 | A | DI1 - 29 | DI1 - A | 16 | TB-5 | 12 | SDKLG1dCB-O | SIDIKALANG 1
30 | 150 | SDKLG1 | CB | Close |  | TSD | 1 | 2 | A | DI1 - 30 | DI1 - A | 35 | TB-5 | 13 | SDKLG1dCB-C | SIDIKALANG 1
31 | 150 | SDKLG1 | BI1 | Open | 0/16/16 | TSD | 1 | 2 | A | DI1 - 31 | DI1 - A | 17 | TB-5 | 14 | SDKLG1dBI1-O | SIDIKALANG 1
32 | 150 | SDKLG1 | BI1 | Close |  | TSD | 1 | 2 | A | DI1 - 32 | DI1 - A | 36 | TB-5 | 15 | SDKLG1dBI1-C | SIDIKALANG 1
33 | 150 | SDKLG1 | BI2 | Open | 0/16/17 | TSD | 1 | 2 | B | DI1 - 33 | DI1 - B | 1 | TB-5 | 16 | SDKLG1dBI2-O | SIDIKALANG 1
34 | 150 | SDKLG1 | BI2 | Close |  | TSD | 1 | 2 | B | DI1 - 34 | DI1 - B | 20 | TB-5 | 17 | SDKLG1dBI2-C | SIDIKALANG 1
35 | 150 | SDKLG1 | LI | Open | 0/16/18 | TSD | 1 | 2 | B | DI1 - 35 | DI1 - B | 2 | TB-5 | 18 | SDKLG1dLI-O | SIDIKALANG 1
36 | 150 | SDKLG1 | LI | Close |  | TSD | 1 | 2 | B | DI1 - 36 | DI1 - B | 21 | TB-5 | 19 | SDKLG1dLI-C | SIDIKALANG 1
37 | 150 | SDKLG1 | ES | Open | 0/16/19 | TSD | 1 | 2 | B | DI1 - 37 | DI1 - B | 3 | TB-5 | 20 | SDKLG1dES-O | SIDIKALANG 1
38 | 150 | SDKLG1 | ES | Close |  | TSD | 1 | 2 | B | DI1 - 38 | DI1 - B | 22 | TB-5 | 21 | SDKLG1dES-C | SIDIKALANG 1
39 | 150 | TELE1 | CB | Open | 0/16/20 | TSD | 1 | 2 | B | DI1 - 39 | DI1 - B | 4 | TB-6 | 12 | TELE1dCB-O | TELE 1
40 | 150 | TELE1 | CB | Close |  | TSD | 1 | 2 | B | DI1 - 40 | DI1 - B | 23 | TB-6 | 13 | TELE1dCB-C | TELE 1
41 | 150 | TELE1 | BI1 | Open | 0/16/21 | TSD | 1 | 2 | B | DI1 - 41 | DI1 - B | 5 | TB-6 | 14 | TELE1dBI1-O | TELE 1
42 | 150 | TELE1 | BI1 | Close |  | TSD | 1 | 2 | B | DI1 - 42 | DI1 - B | 24 | TB-6 | 15 | TELE1dBI1-C | TELE 1
43 | 150 | TELE1 | BI2 | Open | 0/16/22 | TSD | 1 | 2 | B | DI1 - 43 | DI1 - B | 6 | TB-6 | 16 | TELE1dBI2-O | TELE 1
44 | 150 | TELE1 | BI2 | Close |  | TSD | 1 | 2 | B | DI1 - 44 | DI1 - B | 25 | TB-6 | 17 | TELE1dBI2-C | TELE 1
45 | 150 | TELE1 | LI | Open | 0/16/23 | TSD | 1 | 2 | B | DI1 - 45 | DI1 - B | 7 | TB-6 | 18 | TELE1dLI-O | TELE 1
46 | 150 | TELE1 | LI | Close |  | TSD | 1 | 2 | B | DI1 - 46 | DI1 - B | 26 | TB-6 | 19 | TELE1dLI-C | TELE 1
47 | 150 | TELE1 | ES | Open | 0/16/24 | TSD | 1 | 2 | B | DI1 - 47 | DI1 - B | 8 | TB-6 | 20 | TELE1dES-O | TELE 1
48 | 150 | TELE1 | ES | Close |  | TSD | 1 | 2 | B | DI1 - 48 | DI1 - B | 27 | TB-6 | 21 | TELE1dES-C | TELE 1
49 | 150 | PRSEA1 | CB | Open | 0/16/25 | TSD | 1 | 2 | B | DI1 - 49 | DI1 - B | 10 | TB-7 | 12 | PRSEA1dCB-O | PORSEA 1
50 | 150 | PRSEA1 | CB | Close |  | TSD | 1 | 2 | B | DI1 - 50 | DI1 - B | 29 | TB-7 | 13 | PRSEA1dCB-C | PORSEA 1
51 | 150 | PRSEA1 | BI1 | Open | 0/16/26 | TSD | 1 | 2 | B | DI1 - 51 | DI1 - B | 11 | TB-7 | 14 | PRSEA1dBI1-O | PORSEA 1
52 | 150 | PRSEA1 | BI1 | Close |  | TSD | 1 | 2 | B | DI1 - 52 | DI1 - B | 30 | TB-7 | 15 | PRSEA1dBI1-C | PORSEA 1
53 | 150 | PRSEA1 | BI2 | Open | 0/16/27 | TSD | 1 | 2 | B | DI1 - 53 | DI1 - B | 12 | TB-7 | 16 | PRSEA1dBI2-O | PORSEA 1
54 | 150 | PRSEA1 | BI2 | Close |  | TSD | 1 | 2 | B | DI1 - 54 | DI1 - B | 31 | TB-7 | 17 | PRSEA1dBI2-C | PORSEA 1
55 | 150 | PRSEA1 | LI | Open | 0/16/28 | TSD | 1 | 2 | B | DI1 - 55 | DI1 - B | 13 | TB-7 | 18 | PRSEA1dLI-O | PORSEA 1
56 | 150 | PRSEA1 | LI | Close |  | TSD | 1 | 2 | B | DI1 - 56 | DI1 - B | 32 | TB-7 | 19 | PRSEA1dLI-C | PORSEA 1
57 | 150 | PRSEA1 | ES | Open | 0/16/29 | TSD | 1 | 2 | B | DI1 - 57 | DI1 - B | 14 | TB-7 | 20 | PRSEA1dES-O | PORSEA 1
58 | 150 | PRSEA1 | ES | Close |  | TSD | 1 | 2 | B | DI1 - 58 | DI1 - B | 33 | TB-7 | 21 | PRSEA1dES-C | PORSEA 1
59 | 150 | SBLGA1 | CB | Open | 0/16/30 | TSD | 1 | 2 | B | DI1 - 59 | DI1 - B | 15 | TB-8 | 12 | SBLGA1dCB-O | SIBOLGA 1
60 | 150 | SBLGA1 | CB | Close |  | TSD | 1 | 2 | B | DI1 - 60 | DI1 - B | 34 | TB-8 | 13 | SBLGA1dCB-C | SIBOLGA 1
61 | 150 | SBLGA1 | BI1 | Open | 0/16/31 | TSD | 1 | 2 | B | DI1 - 61 | DI1 - B | 16 | TB-8 | 14 | SBLGA1dBI1-O | SIBOLGA 1
62 | 150 | SBLGA1 | BI1 | Close |  | TSD | 1 | 2 | B | DI1 - 62 | DI1 - B | 35 | TB-8 | 15 | SBLGA1dBI1-C | SIBOLGA 1
63 | 150 | SBLGA1 | BI2 | Open | 0/16/32 | TSD | 1 | 2 | B | DI1 - 63 | DI1 - B | 17 | TB-8 | 16 | SBLGA1dBI2-O | SIBOLGA 1
64 | 150 | SBLGA1 | BI2 | Close |  | TSD | 1 | 2 | B | DI1 - 64 | DI1 - B | 36 | TB-8 | 17 | SBLGA1dBI2-C | SIBOLGA 1
65 | 150 | SBLGA1 | LI | Open | 0/16/33 | TSD | 1 | 3 | A | DI2 - 1 | DI2 - A | 1 | TB-8 | 18 | SBLGA1dLI-O | SIBOLGA 1
66 | 150 | SBLGA1 | LI | Close |  | TSD | 1 | 3 | A | DI2 - 2 | DI2 - A | 20 | TB-8 | 19 | SBLGA1dLI-C | SIBOLGA 1
67 | 150 | SBLGA1 | ES | Open | 0/16/34 | TSD | 1 | 3 | A | DI2 - 3 | DI2 - A | 2 | TB-8 | 20 | SBLGA1dES-O | SIBOLGA 1
68 | 150 | SBLGA1 | ES | Close |  | TSD | 1 | 3 | A | DI2 - 4 | DI2 - A | 21 | TB-8 | 21 | SBLGA1dES-C | SIBOLGA 1
69 | 150 | TRF521 | CB | Open | 0/16/35 | TSD | 1 | 3 | A | DI2 - 5 | DI2 - A | 3 | TB-9 | 14 | TRAFO1dCB-O | TRF521
70 | 150 | TRF521 | CB | Close |  | TSD | 1 | 3 | A | DI2 - 6 | DI2 - A | 22 | TB-9 | 15 | TRAFO1dCB-C | TRF521
71 | 150 | TRF521 | BI1 | Open | 0/16/36 | TSD | 1 | 3 | A | DI2 - 7 | DI2 - A | 4 | TB-9 | 16 | TRAFO1dBI1-O | TRF521
72 | 150 | TRF521 | BI1 | Close |  | TSD | 1 | 3 | A | DI2 - 8 | DI2 - A | 23 | TB-9 | 17 | TRAFO1dBI1-C | TRF521
73 | 150 | TRF521 | BI2 | Open | 0/16/37 | TSD | 1 | 3 | A | DI2 - 9 | DI2 - A | 5 | TB-9 | 18 | TRAFO1dBI2-O | TRF521
74 | 150 | TRF521 | BI2 | Close |  | TSD | 1 | 3 | A | DI2 - 10 | DI2 - A | 24 | TB-9 | 19 | TRAFO1dBI2-C | TRF521
75 | 150 | TRF521 | TCC | Auto | 0/16/38 | TSD | 1 | 3 | A | DI2 - 11 | DI2 - A | 6 | TB-9 | 20 | TRAFO1dTCC-A | TRF521
76 | 150 | TRF521 | TCC | Manual |  | TSD | 1 | 3 | A | DI2 - 12 | DI2 - A | 25 | TB-9 | 21 | TRAFO1dTCC-M | TRF521
77 | 150 | TRF522 | CB | Open | 0/16/39 | TSD | 1 | 3 | A | DI2 - 13 | DI2 - A | 7 | TB-10 | 14 | TRAFO2dCB-O | TRF522
78 | 150 | TRF522 | CB | Close |  | TSD | 1 | 3 | A | DI2 - 14 | DI2 - A | 26 | TB-10 | 15 | TRAFO2dCB-C | TRF522
79 | 150 | TRF522 | BI1 | Open | 0/16/40 | TSD | 1 | 3 | A | DI2 - 15 | DI2 - A | 8 | TB-10 | 16 | TRAFO2dBI1-O | TRF522
80 | 150 | TRF522 | BI1 | Close |  | TSD | 1 | 3 | A | DI2 - 16 | DI2 - A | 27 | TB-10 | 17 | TRAFO2dBI1-C | TRF522
81 | 150 | TRF522 | BI2 | Open | 0/16/41 | TSD | 1 | 3 | A | DI2 - 17 | DI2 - A | 10 | TB-10 | 18 | TRAFO2dBI2-O | TRF522
82 | 150 | TRF522 | BI2 | Close |  | TSD | 1 | 3 | A | DI2 - 18 | DI2 - A | 29 | TB-10 | 19 | TRAFO2dBI2-C | TRF522
83 | 150 | TRF522 | TCC | Auto | 0/16/42 | TSD | 1 | 3 | A | DI2 - 19 | DI2 - A | 11 | TB-10 | 20 | TRAFO2dTCC-A | TRF522
84 | 150 | TRF522 | TCC | Manual |  | TSD | 1 | 3 | A | DI2 - 20 | DI2 - A | 30 | TB-10 | 21 | TRAFO2dTCC-M | TRF522
85 | 150 | Common | CD | Enable/Disable | 0/32/1 | TSS | 1 | 3 | A | DI2 - 21 | DI2 - A | 12 | TB-1 | 7 | COMMONdCD | COMMON | 8193
86 | 150 | Common | RTU | On/Off | 0/32/2 | TSS | 1 | 3 | A | DI2 - 22 | DI2 - A | 31 | TB-1 | 8 | COMMONdRTU | COMMON
87 | 150 | Common | COM | On/Off | 0/32/3 | TSS | 1 | 3 | A | DI2 - 23 | DI2 - A | 13 | TB-1 | 9 | COMMONdCOM | COMMON
88 | 150 | Common | SUF | On/Off | 0/32/4 | TSS | 1 | 3 | A | DI2 - 24 | DI2 - A | 32 | TB-1 | 10 | COMMONdSUF | COMMON
89 | 150 | Common | SNF | On/Off | 0/32/5 | TSS | 1 | 3 | A | DI2 - 25 | DI2 - A | 14 | TB-1 | 11 | COMMONdSNF | COMMON
90 | 150 | BSBAR1 | P3 | On/Off | 0/32/6 | TSS | 1 | 3 | A | DI2 - 26 | DI2 - A | 33 | TB-1 | 12 | BSBAR1dP3 | BUSBAR 1
91 | 150 | BSBAR1 | VS | On/Off | 0/32/7 | TSS | 1 | 3 | A | DI2 - 27 | DI2 - A | 15 | TB-1 | 13 | BSBAR1dVS | BUSBAR 1
92 | 150 | BSBAR2 | P3 | On/Off | 0/32/8 | TSS | 1 | 3 | A | DI2 - 28 | DI2 - A | 34 | TB-1 | 14 | BSBAR2dP3 | BUSBAR 2
93 | 150 | BSBAR2 | VS | On/Off | 0/32/9 | TSS | 1 | 3 | A | DI2 - 29 | DI2 - A | 16 | TB-1 | 15 | BSBAR2dVS | BUSBAR 2
94 | 150 | KOPEL | LRCB | Local/Remote | 0/32/10 | TSS | 1 | 3 | A | DI2 - 30 | DI2 - A | 35 | TB-2 | 14 | KOPELdLRC | KOPEL
95 | 150 | KOPEL | BF | On/Off | 0/32/11 | TSS | 1 | 3 | A | DI2 - 31 | DI2 - A | 17 | TB-2 | 15 | KOPELdBF | KOPEL
96 | 150 | KOPEL | BRF | On/Off | 0/32/12 | TSS | 1 | 3 | A | DI2 - 32 | DI2 - A | 36 | TB-2 | 16 | KOPELdBRF | KOPEL
97 | 150 | KOPEL | P2 | On/Off | 0/32/13 | TSS | 1 | 3 | B | DI2 - 33 | DI2 - B | 1 | TB-2 | 17 | KOPELdP2 | KOPEL
98 | 150 | KOPEL | CSP | On/Off | 0/32/14 | TSS | 1 | 3 | B | DI2 - 34 | DI2 - B | 20 | TB-2 | 18 | KOPELdCSP | KOPEL
99 | 150 | PRSEA2 | LRCB | Local/Remote | 0/32/15 | TSS | 1 | 3 | B | DI2 - 35 | DI2 - B | 2 | TB-3 | 22 | PRSEA2dLRC | PORSEA 2
100 | 150 | PRSEA2 | BF | On/Off | 0/32/16 | TSS | 1 | 3 | B | DI2 - 36 | DI2 - B | 21 | TB-3 | 23 | PRSEA2dBF | PORSEA 2
101 | 150 | PRSEA2 | BRF | On/Off | 0/32/17 | TSS | 1 | 3 | B | DI2 - 37 | DI2 - B | 3 | TB-3 | 24 | PRSEA2dBRF | PORSEA 2
102 | 150 | PRSEA2 | P1 | On/Off | 0/32/18 | TSS | 1 | 3 | B | DI2 - 38 | DI2 - B | 22 | TB-3 | 25 | PRSEA2dP1 | PORSEA 2
103 | 150 | PRSEA2 | AR | On/Off | 0/32/19 | TSS | 1 | 3 | B | DI2 - 39 | DI2 - B | 4 | TB-3 | 26 | PRSEA2dAR | PORSEA 2
104 | 150 | PRSEA2 | P2 | On/Off | 0/32/20 | TSS | 1 | 3 | B | DI2 - 40 | DI2 - B | 23 | TB-3 | 27 | PRSEA2dP2 | PORSEA 2
105 | 150 | PRSEA2 | TTT | On/Off | 0/32/21 | TSS | 1 | 3 | B | DI2 - 41 | DI2 - B | 5 | TB-3 | 28 | PRSEA2dTTT | PORSEA 2
106 | 150 | PRSEA2 | TTR | On/Off | 0/32/22 | TSS | 1 | 3 | B | DI2 - 42 | DI2 - B | 24 | TB-3 | 29 | PRSEA2dTTR | PORSEA 2
107 | 150 | PRSEA2 | CSP | On/Off | 0/32/23 | TSS | 1 | 3 | B | DI2 - 43 | DI2 - B | 6 | TB-3 | 30 | PRSEA2dCSP | PORSEA 2
108 | 150 | SBLGA2 | LRCB | Local/Remote | 0/32/24 | TSS | 1 | 3 | B | DI2 - 44 | DI2 - B | 25 | TB-4 | 22 | SBLGA2dLRC | SIBOLGA 2
109 | 150 | SBLGA2 | BF | On/Off | 0/32/25 | TSS | 1 | 3 | B | DI2 - 45 | DI2 - B | 7 | TB-4 | 23 | SBLGA2dBF | SIBOLGA 2
110 | 150 | SBLGA2 | BRF | On/Off | 0/32/26 | TSS | 1 | 3 | B | DI2 - 46 | DI2 - B | 26 | TB-4 | 24 | SBLGA2dBRF | SIBOLGA 2
111 | 150 | SBLGA2 | P1 | On/Off | 0/32/27 | TSS | 1 | 3 | B | DI2 - 47 | DI2 - B | 8 | TB-4 | 25 | SBLGA2dP1 | SIBOLGA 2
112 | 150 | SBLGA2 | AR | On/Off | 0/32/28 | TSS | 1 | 3 | B | DI2 - 48 | DI2 - B | 27 | TB-4 | 26 | SBLGA2dAR | SIBOLGA 2
113 | 150 | SBLGA2 | P2 | On/Off | 0/32/29 | TSS | 1 | 3 | B | DI2 - 49 | DI2 - B | 10 | TB-4 | 27 | SBLGA2dP2 | SIBOLGA 2
114 | 150 | SBLGA2 | TTT | On/Off | 0/32/30 | TSS | 1 | 3 | B | DI2 - 50 | DI2 - B | 29 | TB-4 | 28 | SBLGA2dTTT | SIBOLGA 2
115 | 150 | SBLGA2 | TTR | On/Off | 0/32/31 | TSS | 1 | 3 | B | DI2 - 51 | DI2 - B | 11 | TB-4 | 29 | SBLGA2dTTR | SIBOLGA 2
116 | 150 | SBLGA2 | CSP | On/Off | 0/32/32 | TSS | 1 | 3 | B | DI2 - 52 | DI2 - B | 30 | TB-4 | 30 | SBLGA2dCSP | SIBOLGA 2
117 | 150 | SDKLG1 | LRCB | Local/Remote | 0/32/33 | TSS | 1 | 3 | B | DI2 - 53 | DI2 - B | 12 | TB-5 | 22 | SDKLG1dLRC | SIDIKALANG 1
118 | 150 | SDKLG1 | BF | On/Off | 0/32/34 | TSS | 1 | 3 | B | DI2 - 54 | DI2 - B | 31 | TB-5 | 23 | SDKLG1dBF | SIDIKALANG 1
119 | 150 | SDKLG1 | BRF | On/Off | 0/32/35 | TSS | 1 | 3 | B | DI2 - 55 | DI2 - B | 13 | TB-5 | 24 | SDKLG1dBRF | SIDIKALANG 1
120 | 150 | SDKLG1 | P1 | On/Off | 0/32/36 | TSS | 1 | 3 | B | DI2 - 56 | DI2 - B | 32 | TB-5 | 25 | SDKLG1dP1 | SIDIKALANG 1
121 | 150 | SDKLG1 | AR | On/Off | 0/32/37 | TSS | 1 | 3 | B | DI2 - 57 | DI2 - B | 14 | TB-5 | 26 | SDKLG1dAR | SIDIKALANG 1
122 | 150 | SDKLG1 | P2 | On/Off | 0/32/38 | TSS | 1 | 3 | B | DI2 - 58 | DI2 - B | 33 | TB-5 | 27 | SDKLG1dP2 | SIDIKALANG 1
123 | 150 | SDKLG1 | TTT | On/Off | 0/32/39 | TSS | 1 | 3 | B | DI2 - 59 | DI2 - B | 15 | TB-5 | 28 | SDKLG1dTTT | SIDIKALANG 1
124 | 150 | SDKLG1 | TTR | On/Off | 0/32/40 | TSS | 1 | 3 | B | DI2 - 60 | DI2 - B | 34 | TB-5 | 29 | SDKLG1dTTR | SIDIKALANG 1
125 | 150 | SDKLG1 | CSP | On/Off | 0/32/41 | TSS | 1 | 3 | B | DI2 - 61 | DI2 - B | 16 | TB-5 | 30 | SDKLG1dCSP | SIDIKALANG 1
126 | 150 | TELE1 | LRCB | Local/Remote | 0/32/42 | TSS | 1 | 3 | B | DI2 - 62 | DI2 - B | 35 | TB-6 | 22 | TELE1dLRC | TELE 1
127 | 150 | TELE1 | BF | On/Off | 0/32/43 | TSS | 1 | 3 | B | DI2 - 63 | DI2 - B | 17 | TB-6 | 23 | TELE1dBF | TELE 1
128 | 150 | TELE1 | BRF | On/Off | 0/32/44 | TSS | 1 | 3 | B | DI2 - 64 | DI2 - B | 36 | TB-6 | 24 | TELE1dBRF | TELE 1
129 | 150 | TELE1 | P1 | On/Off | 0/32/45 | TSS | 1 | 4 | A | DI3 - 1 | DI3 - A | 1 | TB-6 | 25 | TELE1dP1 | TELE 1
130 | 150 | TELE1 | AR | On/Off | 0/32/46 | TSS | 1 | 4 | A | DI3 - 2 | DI3 - A | 20 | TB-6 | 26 | TELE1dAR | TELE 1
131 | 150 | TELE1 | P2 | On/Off | 0/32/47 | TSS | 1 | 4 | A | DI3 - 3 | DI3 - A | 2 | TB-6 | 27 | TELE1dP2 | TELE 1
132 | 150 | TELE1 | TTT | On/Off | 0/32/48 | TSS | 1 | 4 | A | DI3 - 4 | DI3 - A | 21 | TB-6 | 28 | TELE1dTTT | TELE 1
133 | 150 | TELE1 | TTR | On/Off | 0/32/49 | TSS | 1 | 4 | A | DI3 - 5 | DI3 - A | 3 | TB-6 | 29 | TELE1dTTR | TELE 1
134 | 150 | TELE1 | CSP | On/Off | 0/32/50 | TSS | 1 | 4 | A | DI3 - 6 | DI3 - A | 22 | TB-6 | 30 | TELE1dCSP | TELE 1
135 | 150 | PRSEA1 | LRCB | Local/Remote | 0/32/51 | TSS | 1 | 4 | A | DI3 - 7 | DI3 - A | 4 | TB-7 | 22 | PRSEA1dLRC | PORSEA 1
136 | 150 | PRSEA1 | LRBI1 | Local/Remote | 0/32/52 | TSS | 1 | 4 | A | DI3 - 8 | DI3 - A | 23 | TB-7 | 23 | PRSEA1dLR1 | PORSEA 1
137 | 150 | PRSEA1 | LRBI2 | Local/Remote | 0/32/53 | TSS | 1 | 4 | A | DI3 - 9 | DI3 - A | 5 | TB-7 | 24 | PRSEA1dLR2 | PORSEA 1
138 | 150 | PRSEA1 | BF | On/Off | 0/32/54 | TSS | 1 | 4 | A | DI3 - 10 | DI3 - A | 24 | TB-7 | 25 | PRSEA1dBF | PORSEA 1
139 | 150 | PRSEA1 | BRF | On/Off | 0/32/55 | TSS | 1 | 4 | A | DI3 - 11 | DI3 - A | 6 | TB-7 | 26 | PRSEA1dBRF | PORSEA 1
140 | 150 | PRSEA1 | P1 | On/Off | 0/32/56 | TSS | 1 | 4 | A | DI3 - 12 | DI3 - A | 25 | TB-7 | 27 | PRSEA1dP1 | PORSEA 1
141 | 150 | PRSEA1 | AR | On/Off | 0/32/57 | TSS | 1 | 4 | A | DI3 - 13 | DI3 - A | 7 | TB-7 | 28 | PRSEA1dAR | PORSEA 1
142 | 150 | PRSEA1 | P2 | On/Off | 0/32/58 | TSS | 1 | 4 | A | DI3 - 14 | DI3 - A | 26 | TB-7 | 29 | PRSEA1dP2 | PORSEA 1
143 | 150 | PRSEA1 | TTT | On/Off | 0/32/59 | TSS | 1 | 4 | A | DI3 - 15 | DI3 - A | 8 | TB-7 | 30 | PRSEA1dTTT | PORSEA 1
144 | 150 | PRSEA1 | TTR | On/Off | 0/32/60 | TSS | 1 | 4 | A | DI3 - 16 | DI3 - A | 27 | TB-7 | 31 | PRSEA1dTTR | PORSEA 1
145 | 150 | PRSEA1 | CSP | On/Off | 0/32/61 | TSS | 1 | 4 | A | DI3 - 17 | DI3 - A | 10 | TB-7 | 32 | PRSEA1dCSP | PORSEA 1
146 | 150 | SBLGA1 | LRCB | Local/Remote | 0/32/62 | TSS | 1 | 4 | A | DI3 - 18 | DI3 - A | 29 | TB-8 | 22 | SBLGA1dLRC | SIBOLGA 1
147 | 150 | SBLGA1 | LRBI1 | Local/Remote | 0/32/63 | TSS | 1 | 4 | A | DI3 - 19 | DI3 - A | 11 | TB-8 | 23 | SBLGA1dLR1 | SIBOLGA 1
148 | 150 | SBLGA1 | LRBI2 | Local/Remote | 0/32/64 | TSS | 1 | 4 | A | DI3 - 20 | DI3 - A | 30 | TB-8 | 24 | SBLGA1dLR2 | SIBOLGA 1
149 | 150 | SBLGA1 | BF | On/Off | 0/32/65 | TSS | 1 | 4 | A | DI3 - 21 | DI3 - A | 12 | TB-8 | 25 | SBLGA1dBF | SIBOLGA 1
150 | 150 | SBLGA1 | BRF | On/Off | 0/32/66 | TSS | 1 | 4 | A | DI3 - 22 | DI3 - A | 31 | TB-8 | 26 | SBLGA1dBRF | SIBOLGA 1
151 | 150 | SBLGA1 | P1 | On/Off | 0/32/67 | TSS | 1 | 4 | A | DI3 - 23 | DI3 - A | 13 | TB-8 | 27 | SBLGA1dP1 | SIBOLGA 1
152 | 150 | SBLGA1 | AR | On/Off | 0/32/68 | TSS | 1 | 4 | A | DI3 - 24 | DI3 - A | 32 | TB-8 | 28 | SBLGA1dAR | SIBOLGA 1
153 | 150 | SBLGA1 | P2 | On/Off | 0/32/69 | TSS | 1 | 4 | A | DI3 - 25 | DI3 - A | 14 | TB-8 | 29 | SBLGA1dP2 | SIBOLGA 1
154 | 150 | SBLGA1 | TTT | On/Off | 0/32/70 | TSS | 1 | 4 | A | DI3 - 26 | DI3 - A | 33 | TB-8 | 30 | SBLGA1dTTT | SIBOLGA 1
155 | 150 | SBLGA1 | TTR | On/Off | 0/32/71 | TSS | 1 | 4 | A | DI3 - 27 | DI3 - A | 15 | TB-8 | 31 | SBLGA1dTTR | SIBOLGA 1
156 | 150 | SBLGA1 | CSP | On/Off | 0/32/72 | TSS | 1 | 4 | A | DI3 - 28 | DI3 - A | 34 | TB-8 | 32 | SBLGA1dCSP | SIBOLGA 1
157 | 150 | TRF521 | LRCB | Local/Remote | 0/32/73 | TSS | 1 | 4 | A | DI3 - 29 | DI3 - A | 16 | TB-9 | 22 | TRAFO1dLRC | TRF521
158 | 150 | TRF521 | LRBI1 | Local/Remote | 0/32/74 | TSS | 1 | 4 | A | DI3 - 30 | DI3 - A | 35 | TB-9 | 23 | TRAFO1dLR1 | TRF521
159 | 150 | TRF521 | LRBI2 | Local/Remote | 0/32/75 | TSS | 1 | 4 | A | DI3 - 31 | DI3 - A | 17 | TB-9 | 24 | TRAFO1dLR2 | TRF521
160 | 150 | TRF521 | LRTC | Local/Remote | 0/32/76 | TSS | 1 | 4 | A | DI3 - 32 | DI3 - A | 36 | TB-9 | 25 | TRAFO1dLRT | TRF521
161 | 150 | TRF521 | BF | On/Off | 0/32/77 | TSS | 1 | 4 | B | DI3 - 33 | DI3 - B | 1 | TB-9 | 26 | TRAFO1dBF | TRF521
162 | 150 | TRF521 | BRF | On/Off | 0/32/78 | TSS | 1 | 4 | B | DI3 - 34 | DI3 - B | 20 | TB-9 | 27 | TRAFO1dBRF | TRF521
163 | 150 | TRF521 | TRA | On/Off | 0/32/79 | TSS | 1 | 4 | B | DI3 - 35 | DI3 - B | 2 | TB-9 | 28 | TRAFO1dTRA | TRF521
164 | 150 | TRF521 | TRT | On/Off | 0/32/80 | TSS | 1 | 4 | B | DI3 - 36 | DI3 - B | 21 | TB-9 | 29 | TRAFO1dTRT | TRF521
165 | 150 | TRF521 | TCT | On/Off | 0/32/81 | TSS | 1 | 4 | B | DI3 - 37 | DI3 - B | 3 | TB-9 | 30 | TRAFO1dTCT | TRF521
166 | 150 | TRF521 | TCA | On/Off | 0/32/82 | TSS | 1 | 4 | B | DI3 - 38 | DI3 - B | 22 | TB-9 | 31 | TRAFO1dTCA | TRF521
167 | 150 | TRF521 | TCH | On/Off | 0/32/83 | TSS | 1 | 4 | B | DI3 - 39 | DI3 - B | 4 | TB-9 | 32 | TRAFO1dTCH | TRF521
168 | 150 | TRF521 | TCL | On/Off | 0/32/84 | TSS | 1 | 4 | B | DI3 - 40 | DI3 - B | 23 | TB-9 | 33 | TRAFO1dTCL | TRF521
169 | 150 | TRF521 | TEA | On/Off | 0/32/85 | TSS | 1 | 4 | B | DI3 - 41 | DI3 - B | 5 | TB-9 | 34 | TRAFO1dTEA | TRF521
170 | 150 | TRF521 | TET | On/Off | 0/32/86 | TSS | 1 | 4 | B | DI3 - 42 | DI3 - B | 24 | TB-9 | 35 | TRAFO1dTET | TRF521
171 | 150 | TRF522 | LRCB | Local/Remote | 0/32/87 | TSS | 1 | 4 | B | DI3 - 43 | DI3 - B | 6 | TB-10 | 22 | TRAFO2dLRC | TRF522
172 | 150 | TRF522 | LRTC | Local/Remote | 0/32/88 | TSS | 1 | 4 | B | DI3 - 44 | DI3 - B | 25 | TB-10 | 23 | TRAFO2dLRT | TRF522
173 | 150 | TRF522 | BF | On/Off | 0/32/89 | TSS | 1 | 4 | B | DI3 - 45 | DI3 - B | 7 | TB-10 | 24 | TRAFO2dBF | TRF522
174 | 150 | TRF522 | BRF | On/Off | 0/32/90 | TSS | 1 | 4 | B | DI3 - 46 | DI3 - B | 26 | TB-10 | 25 | TRAFO2dBRF | TRF522
175 | 150 | TRF522 | TRA | On/Off | 0/32/91 | TSS | 1 | 4 | B | DI3 - 47 | DI3 - B | 8 | TB-10 | 26 | TRAFO2dTRA | TRF522
176 | 150 | TRF522 | TRT | On/Off | 0/32/92 | TSS | 1 | 4 | B | DI3 - 48 | DI3 - B | 27 | TB-10 | 27 | TRAFO2dTRT | TRF522
177 | 150 | TRF522 | TCT | On/Off | 0/32/93 | TSS | 1 | 4 | B | DI3 - 49 | DI3 - B | 10 | TB-10 | 28 | TRAFO2dTCT | TRF522
178 | 150 | TRF522 | TCA | On/Off | 0/32/94 | TSS | 1 | 4 | B | DI3 - 50 | DI3 - B | 29 | TB-10 | 29 | TRAFO2dTCA | TRF522
179 | 150 | TRF522 | TCH | On/Off | 0/32/95 | TSS | 1 | 4 | B | DI3 - 51 | DI3 - B | 11 | TB-10 | 30 | TRAFO2dTCH | TRF522
180 | 150 | TRF522 | TCL | On/Off | 0/32/96 | TSS | 1 | 4 | B | DI3 - 52 | DI3 - B | 30 | TB-10 | 31 | TRAFO2dTCL | TRF522
181 | 150 | TRF522 | TEA | On/Off | 0/32/97 | TSS | 1 | 4 | B | DI3 - 53 | DI3 - B | 12 | TB-10 | 32 | TRAFO2dTEA | TRF522
182 | 150 | TRF522 | TET | On/Off | 0/32/98 | TSS | 1 | 4 | B | DI3 - 54 | DI3 - B | 31 | TB-10 | 33 | TRAFO2dTET | TRF522
183 | 20 | INCTD-1 | CB | Open | 0/16/43 | TSD | 1 | 4 | B | DI3 - 55 | DI3 - B | 13
184 | 20 | INCTD-1 | CB | Close |  | TSD | 1 | 4 | B | DI3 - 56 | DI3 - B | 32
185 | 20 | INCTD-2 | CB | Open | 0/16/44 | TSD | 1 | 4 | B | DI3 - 57 | DI3 - B | 14
186 | 20 | INCTD-2 | CB | Close |  | TSD | 1 | 4 | B | DI3 - 58 | DI3 - B | 33
187 | 20 | INCTD-1 | LRCB | Local/Remote | 0/32/99 | TSS | 1 | 4 | B | DI3 - 59 | DI3 - B | 15
188 | 20 | INCTD-2 | LRCB | Local/Remote | 0/32/100 | TSS | 1 | 4 | B | DI3 - 60 | DI3 - B | 34
189 | 150 | PORSEA-1 | HTP | On/Off | 0/32/101 | TSS | 1 | 4 | B | DI3 - 61 | DI3 - B | 16 |  |  | HTP PORSEA
190 | 151 | SIBOLGA-1 | HTP | On/Off | 0/32/103 | TSS | 1 | 4 | B | DI3 - 62 | DI3 - B | 35 |  |  | HTP SIBOLGA
191 | 152 | SIDIKALANG (DOSA) | HTP | On/Off | 0/32/105 | TSS | 1 | 4 | B | DI3 - 63 | DI3 - B | 17 |  |  | HTP DOSA
192 | 153 | TELE | HTP | On/Off | 0/32/106 | TSS | 1 | 4 | B | DI3 - 64 | DI3 - B | 36 |  |  | HTP TELE
|  |  |  | 4096 | 0/16/0
|  |  |  | 4139 | 0/16/43
|  |  |  | 4140 | 0/16/44
|  |  |  | 4141 | 0/16/45
|  |  |  | 8192 | 0/32/0
|  |  |  | 8291 | 0/32/99
|  |  |  | 8292 | 0/32/100
|  |  |  | 8293 | 0/32/101
|  |  |  | 8294 | 0/32/102
|  |  |  | 8295 | 0/32/103 | 8295
|  |  |  | 8296 | 0/32/104
|  |  |  | 8297 | 0/32/105

## IED
Proyek |  | : REHABILITASI DAN PENGADAAN SCADA SISTEM SUMUT - ACEH | [8 empty] | No. Dokumen : | INSTP/RTU
Customer |  | : PT PLN (PERSERO) PENYALURAN & PUSAT PENGATUR BEBAN SUMATERA | [8 empty] | Revisi : | 1
No Kontrak PLN |  | : 002.PJ/612/GM.P3B-Sumatera/2006
Kontraktor |  | : PT. SIEMENS INDONESIA
No Kontrak Siemens |  | : 340P-30064 | [8 empty] | Tanggal : | 10 April 2007
RTU WIRING & AFFECTATION MODULES
Name of Substation |  | : TARUTUNG
Number of CPU |  | : 2
Name of Module |  | : -
NO | DATABASE |  |  |  | ADDRESS | TYPE DATA | CELL NUMBER | CPU NUMBER | RS232 PORT NUMBER | IED NUMBER | REMARKS
| VOLTAGE | BAY NAME | DEVICE | DATA
1 | 150 | BSBAR1 | KV | KV | 0/12/1 | TM | 1 | 1 | 3 | 1 | IED Meter Busbar 1
2 | 150 | BSBAR1 | Hz | Hz | 0/12/2 | TM | 1 | 1 | 3 | 1 | IED Meter Busbar 1
3 | 150 | BSBAR2 | KV | KV | 0/12/3 | TM | 1 | 1 | 3 | 2 | IED Meter Busbar 2
4 | 150 | BSBAR2 | Hz | Hz | 0/12/4 | TM | 1 | 1 | 3 | 2 | IED Meter Busbar 2
5 | 150 | PRSEA-2 | MW | MW | 0/12/5 | TM | 1 | 1 | 3 | 3 | IED Meter PORSEA 2
6 | 150 | PRSEA-2 | MQ | MQ | 0/12/6 | TM | 1 | 1 | 3 | 3 | IED Meter PORSEA 2
7 | 150 | PRSEA-2 | A | A | 0/12/7 | TM | 1 | 1 | 3 | 3 | IED Meter PORSEA 2
8 | 150 | PRSEA-2 | KV | KV | 0/12/8 | TM | 1 | 1 | 3 | 3 | IED Meter PORSEA 2
9 | 150 | PRSEA-2 | Hz | Hz | 0/12/9 | TM | 1 | 1 | 3 | 3 | IED Meter PORSEA 2
10 | 150 | SBLGA-2 | MW | MW | 0/12/10 | TM | 1 | 1 | 3 | 4 | IED Meter SIBOLGA 2
11 | 150 | SBLGA-2 | MQ | MQ | 0/12/11 | TM | 1 | 1 | 3 | 4 | IED Meter SIBOLGA 2
12 | 150 | SBLGA-2 | A | A | 0/12/12 | TM | 1 | 1 | 3 | 4 | IED Meter SIBOLGA 2
13 | 150 | SBLGA-2 | KV | KV | 0/12/13 | TM | 1 | 1 | 3 | 4 | IED Meter SIBOLGA 2
14 | 150 | SBLGA-2 | Hz | Hz | 0/12/14 | TM | 1 | 1 | 3 | 4 | IED Meter SIBOLGA 2
15 | 150 | SDKLG-1 | MW | MW | 0/12/15 | TM | 1 | 1 | 3 | 5 | IED Meter SIDIKALANG 1
16 | 150 | SDKLG-1 | MQ | MQ | 0/12/16 | TM | 1 | 1 | 3 | 5 | IED Meter SIDIKALANG 1
17 | 150 | SDKLG-1 | A | A | 0/12/17 | TM | 1 | 1 | 3 | 5 | IED Meter SIDIKALANG 1
18 | 150 | SDKLG-1 | KV | KV | 0/12/18 | TM | 1 | 1 | 3 | 5 | IED Meter SIDIKALANG 1
19 | 150 | SDKLG-1 | Hz | Hz | 0/12/19 | TM | 1 | 1 | 3 | 5 | IED Meter SIDIKALANG 1
20 | 150 | TELE-1 | MW | MW | 0/12/20 | TM | 1 | 1 | 3 | 6 | IED Meter TELE 1
21 | 150 | TELE-1 | MQ | MQ | 0/12/21 | TM | 1 | 1 | 3 | 6 | IED Meter TELE 1
22 | 150 | TELE-1 | A | A | 0/12/22 | TM | 1 | 1 | 3 | 6 | IED Meter TELE 1
23 | 150 | TELE-1 | KV | KV | 0/12/23 | TM | 1 | 1 | 3 | 6 | IED Meter TELE 1
24 | 150 | TELE-1 | Hz | Hz | 0/12/24 | TM | 1 | 1 | 3 | 6 | IED Meter TELE 1
25 | 150 | PRSEA-1 | MW | MW | 0/12/25 | TM | 1 | 1 | 3 | 7 | IED Meter PORSEA 1
26 | 150 | PRSEA-1 | MQ | MQ | 0/12/26 | TM | 1 | 1 | 3 | 7 | IED Meter PORSEA 1
27 | 150 | PRSEA-1 | A | A | 0/12/27 | TM | 1 | 1 | 3 | 7 | IED Meter PORSEA 1
28 | 150 | PRSEA-1 | KV | KV | 0/12/28 | TM | 1 | 1 | 3 | 7 | IED Meter PORSEA 1
29 | 150 | PRSEA-1 | Hz | Hz | 0/12/29 | TM | 1 | 1 | 3 | 7 | IED Meter PORSEA 1
30 | 150 | SBLGA-1 | MW | MW | 0/12/30 | TM | 1 | 1 | 3 | 8 | IED Meter SIBOLGA 1
31 | 150 | SBLGA-1 | MQ | MQ | 0/12/31 | TM | 1 | 1 | 3 | 8 | IED Meter SIBOLGA 1
32 | 150 | SBLGA-1 | A | A | 0/12/32 | TM | 1 | 1 | 3 | 8 | IED Meter SIBOLGA 1
33 | 150 | SBLGA-1 | KV | KV | 0/12/33 | TM | 1 | 1 | 3 | 8 | IED Meter SIBOLGA 1
34 | 150 | SBLGA-1 | Hz | Hz | 0/12/34 | TM | 1 | 1 | 3 | 8 | IED Meter SIBOLGA 1
35 | 150 | TRF52-1 | MW | MW | 0/12/35 | TM | 2 | 2 | 3 | 9 | IED Meter Trafo TD 1
36 | 150 | TRF52-1 | MQ | MQ | 0/12/36 | TM | 2 | 2 | 3 | 9 | IED Meter Trafo TD 1
37 | 150 | TRF52-1 | A | A | 0/12/37 | TM | 2 | 2 | 3 | 9 | IED Meter Trafo TD 1
38 | 150 | TRF52-1 | KV | KV | 0/12/38 | TM | 2 | 2 | 3 | 9 | IED Meter Trafo TD 1
39 | 150 | TRF52-1 | Hz | Hz | 0/12/39 | TM | 2 | 2 | 3 | 9 | IED Meter Trafo TD 1
40 | 150 | TRF52-2 | MW | MW | 0/12/40 | TM | 2 | 2 | 3 | 10 | IED Meter Trafo TD 2
41 | 150 | TRF52-2 | MQ | MQ | 0/12/41 | TM | 2 | 2 | 3 | 10 | IED Meter Trafo TD 2
42 | 150 | TRF52-2 | A | A | 0/12/42 | TM | 2 | 2 | 3 | 10 | IED Meter Trafo TD 2
43 | 150 | TRF52-2 | KV | KV | 0/12/43 | TM | 2 | 2 | 3 | 10 | IED Meter Trafo TD 2
44 | 150 | TRF52-2 | Hz | Hz | 0/12/44 | TM | 2 | 2 | 3 | 10 | IED Meter Trafo TD 2
45 | 20 | INCTD-1 | MW | MW | 0/12/45 | TM | 2 | 2 | 3 | 11 | IED Meter Incoming TD 1
46 | 20 | INCTD-1 | MQ | MQ | 0/12/46 | TM | 2 | 2 | 3 | 11 | IED Meter Incoming TD 1
47 | 20 | INCTD-1 | A | A | 0/12/47 | TM | 2 | 2 | 3 | 11 | IED Meter Incoming TD 1
48 | 20 | INCTD-1 | KV | KV | 0/12/48 | TM | 2 | 2 | 3 | 11 | IED Meter Incoming TD 1
49 | 20 | INCTD-1 | Hz | Hz | 0/12/49 | TM | 2 | 2 | 3 | 11 | IED Meter Incoming TD 1
50 | 20 | INCTD-2 | MW | MW | 0/12/50 | TM | 2 | 2 | 3 | 12 | IED Meter Incoming TD 2
51 | 20 | INCTD-2 | MQ | MQ | 0/12/51 | TM | 2 | 2 | 3 | 12 | IED Meter Incoming TD 2
52 | 20 | INCTD-2 | A | A | 0/12/52 | TM | 2 | 2 | 3 | 12 | IED Meter Incoming TD 2
53 | 20 | INCTD-2 | KV | KV | 0/12/53 | TM | 2 | 2 | 3 | 12 | IED Meter Incoming TD 2
54 | 20 | INCTD-2 | Hz | Hz | 0/12/54 | TM | 2 | 2 | 3 | 12 | IED Meter Incoming TD 2
|  |  |  | 3072 | 0/12/0
|  |  |  | 3117 | 0/12/45
|  |  |  | 3118 | 0/12/46
|  |  |  | 3119 | 0/12/47
|  |  |  | 3120 | 0/12/48
|  |  |  | 3121 | 0/12/49
|  |  |  | 3122 | 0/12/50
|  |  |  | 3123 | 0/12/51
|  |  |  | 3124 | 0/12/52
|  |  |  | 3125 | 0/12/53
|  |  |  | 3126 | 0/12/54